## Slide 1
FINAL YEAR PROJECT
Smart Solar Load
Priority System
Keeping the important things on
when the sun goes down
[Your name] · Supervisor: [Supervisor's name] · [Department, university]
Notes: Introduce yourself and the project in one sentence: a small, cheap controller that decides which appliances a solar battery keeps running as it empties, so the important ones last much longer.

## Slide 2
THE PROBLEM
When a solar battery runs flat, the whole house goes dark at once, security light included.
The battery charges by day and drains at night. If everything stays on, nothing is saved for the things that matter.
Notes: Keep this simple. Everyone in the room has lived through the lights going out. The question is not whether the battery empties, but what is still running when it does.

## Slide 3
The idea: switch off the least important things first
18 hours
of security light and phone charging from the last stretch of charge, with this system
3.5 hours
from the same charge if every appliance is left on
Estimated from the load schedule for a 200 Ah, 48 V battery; not yet measured.
Notes: This is the headline. The same battery, the same last stretch of charge: roughly five times longer for the things that keep people safe. Be clear it is a calculated estimate from the load schedule, not a measurement.

## Slide 4
Every appliance goes in one of three groups
Critical
Would someone get hurt, or something spoil?
Security light, corridor light, phone and radio charging
Green light in the demo
Essential
Harder to live without, but nobody is harmed?
Ceiling fan, room lighting, refrigerator
Yellow light in the demo
Non-essential
Comfort, entertainment or decoration?
Decorative lights, TV, toilet light, extra bulbs in a lit room
Red light in the demo
Notes: Each appliance is placed by asking one question: what happens if it is off for an hour? The supervisor's examples: four bulbs in one room is waste, the toilet light only needs to be on when someone uses it, and the fan is essential but not critical. Each group is wired through its own relay, an electric switch the controller can flip.

## Slide 5
Groups are decided by what happens if it goes off, not by how much power it uses
At home
Kitchen fridge = Essential
Food keeps for a few hours
In a hospital
Vaccine fridge = Critical
Stock is lost within hours
Notes: The supervisor works in a hospital and suggested it as a setting. It is the clearest illustration: the same kind of fridge moves group because the consequence changes. Only the appliance list in the program changes; the logic stays the same.

## Slide 6
It reads the battery like a fuel gauge
Only part of a battery's voltage range is safe to use. The controller turns that usable portion into a percentage.
30.0 V = 0 %
Empty
40.75 V = 50 %
Halfway
51.5 V = 100 %
Full
It also allows for voltage sag when a heavy load starts, and averages 50 readings a second, so one noisy reading can't flip a switch.
Notes: Supervisor's handwritten note: every battery has a usable portion, 51.5 V at full down to 30.0 V, a span of 21.5 V, split into three tiers by percentage. Voltage sag is like a tap losing pressure when another tap opens: the controller adds the dip back so a fridge starting up doesn't look like the battery emptying.

## Slide 7
As the battery drains, one group goes off at a time
100–66 %
Everything runs · 12.8 A
Critical · Essential · Non-ess.
66–33 %
Non-essential off · 8.3 A
Critical · Essential
33–10 %
Only Critical on · 2.5 A
Critical
Below 10 %
All off: battery protected · 0 A
Nothing: waiting for sun
When the sun returns, they come back in reverse order: most important first.
Notes: Walk down the ladder. At 66 % the decoration, TV and spare bulbs go off and nobody notices yet. At 33 % the fan, room lights and fridge go off. At 10 % even the critical group goes off, and that is to protect the battery from damage, not to save energy. The right-hand column is what is still powered.

## Slide 8
Like a thermostat, it doesn't flick on and off
The first version switched off and on at one voltage. The load pulled the voltage down, it switched off, the voltage recovered, it switched on again: thousands of times a second.
A gap between off and on
Off at 66 %, back on only at 73 %
Wait before acting
A brief dip is ignored; switching back waits longer
A rest period per switch
Each relay has a minimum time between changes
One switch at a time
Two groups never switch at the same instant
Notes: A relay switched thousands of times a second burns out within minutes, so this was the most serious defect in the first prototype. The demo uses fast timings (0.6 s to switch off, 1.5 s to switch back on). In a real house it waits 3 s and 30 s. Type "slow" to show the real-house timings and explain why the real deployment is patient.

## Slide 9
It also acts as a smart circuit breaker
When too much current is drawn
Above 20 A for a moment: Essential and Non-essential go off. A motor's start-up surge doesn't set it off.
Above 26 A: off instantly.
Critical stays on. Too many appliances is not a flat battery.
Three trips in a row = a real fault. It stops retrying until reset.
What the buzzer means
Sound | Meaning
Fast beeping | Overload
Slow toll | Battery nearly empty
Chirp | Below 20 %
Silent | All normal
Notes: The cool-down: after an overload the groups stay off for a while, then come back. If it happens three times in a row the controller treats it as a real fault and stops cycling the relays; someone has to type reset. The buzzer lets you tell what is wrong without looking at the screen.

## Slide 10
Live demo: draining the battery on command
Type | You will see | Because
soc 100 | All three lights on, fan spinning | Full battery: everything runs
soc 60 | Red light goes out | Below 66 %
soc 30 | Yellow light out, fan stops | Below 33 %
soc 5 | Green light out, buzzer tolls | Below 10 %: protect the battery
soc 100 | Groups return one by one | Most important first
The screen shows volts, amps and battery %, e.g. 44.2V 6.4A 78%, and which groups are on.
Notes: "soc" means state of charge. Typing it tells the controller to act as if the battery were at that level, because hitting an exact percentage with a slider looks unconvincing. The demo runs in the Wokwi simulator; the same program runs on the real board. The simulator has no fan part, so a small motor on screen stands in for it; the bench model uses a real 12 V fan. Optional extras: push the load slider past 26 A for an overload trip, then type "status" for the full settings table.

## Slide 11
Built from cheap parts you can buy locally
₦24,000
for the control electronics
About ₦47,000 with a bench model to demonstrate on
Part | What it does
ESP32 board | The brain: reads and decides
16×2 LCD screen | Shows volts, amps, battery %
4-channel relay board | The switches for each group
ACS712 sensor | Measures current drawn
48 V to 5 V converter | Powers the electronics
Buzzer, LEDs, resistors | Alarm and indicator lights
Indicative prices from Alaba and Computer Village; confirm before quoting in the report.
Notes: Supervisor: "Whatever component you are using, you should be able to get it physically, at a cheap price." Everything here is a common through-hole part or ready-made module; nothing is imported and nothing needs special tools beyond a soldering iron. A commercial battery-management system costs 150,000 naira or more, and would do the job for us, leaving nothing to demonstrate.

## Slide 12
Every change traces back to the supervisor's review
The supervisor asked for | Before | After
A real battery's usable portion | Fixed 11, 12, 13 V cut-offs | 30.0–51.5 V range, decisions in %
Critical, essential, non-essential | High, Medium, Low, no appliances | Three groups with real appliances
See each load go off at its % | Screen showed raw volts | Screen shows %, every switch logged
Cheap, buyable parts | Never costed | About ₦24,000, all local
More than LEDs: add a motor | Three indicator lights | A fan on the Essential relay
Fixing these also caught the on-off flicker, and a wiring mistake that left the Critical light on permanently.
Notes: This slide shows the review was taken seriously. The wiring mistake matters: the Critical light was tied straight to the power rail, so it could never go out, which hid the most important event in the demo.

## Slide 13
Honest limits, and what could come next
Count the charge
Voltage is a rough gauge. Counting current in and out is more accurate.
Measure the battery
Curves come from published figures; drain the real one and log it.
Watch the sun
40 % at 7 a.m. is not 40 % at 6 p.m. Measure the panel too.
Time and motion
Toilet light on a motion sensor (about ₦1,500); security light at night only.
Phone dashboard
The board's Wi-Fi is unused; no extra parts needed.
Manual override
Let the user force a group on or off, with a timeout.
Notes: Say these before the panel does. The first two turn the percentages from estimates into measurements. The toilet-light point answers the supervisor directly: it is about someone using it, not about battery level.

## Slide 14
Thank you. Questions?
1. Three groups, decided by consequence
2. Switched off by battery %, least important first
3. About ₦24,000 of locally available parts
Notes: Likely questions. Why 30 V as empty? It is the range the supervisor specified; it is low for real batteries (lithium protection cuts out near 40 V, lead-acid would be damaged), and settings for both are built in, switchable with one line. Why not switch back on at the same point? The relay would cycle and burn out. What if the fridge motor dips the voltage? It waits and allows for the dip. Why doesn't an overload cut Critical? Overload means too many appliances, not an empty battery. Other settings? Yes, a hospital: only the appliance list changes.